## Slide 1: NIAHO® Accreditation for Hospitals Challenges in the Physical Environment
Kelly Proctor CHFM, CHSP
Physical Environment Sector Lead

## Slide 2: Learning Objectives for this Session
This session will enable the attendee to:
  Describe the DNV Physical Environment survey process, including unique methods.
  Outline how integration of ISO 9001-2015 requirements affects development of a hospital’s system management procedures.
  Discuss in depth the current issues, common findings, code clarifications and infection control integration into NIAHO® Facility Management systems
  Discuss the corrective action plan and appeals process actions expected of DNV client hospitals as a result of NIAHO survey findings.

## Slide 3: Expanded international network
16,000
employees
2,500
Mill. EURO (2012)
100
countries
Americas
2500 staff
Asia / Oceania
3500 staff
Europe / Africa / Middle East
10,000 staff
DNV
GL
Notes: Revenue Increased revenue enables better service, more effective network, more R&D, better set up to be at the forefront of development
Global presence Extended network of offices Close to the customers’ needs
Employees Highly educated employees More than 80% of employees have a university degree Better positioned in the global fight for talent

## Slide 4: A world leading certification body
2,200
2,200 healthcare-related organisations have had their quality management system certified by us
Top 3
One of the world’s top three certification bodies for management systems, products, persons and facilities
70,000
More than 70,000 management system (ISO 9001, IS0 14001, etc.) certificates under more than 80 accreditations
6,000
Certified more than 6,000 food companies helping them ensure quality and safety from farm to fork
Notes: We are one of the world's leading certification bodies/registrars offering the latest in management systems certification services.
More than 70,000 certificates issued worldwide.
A commitment to safety, quality, and concern for the environment.
For years, we have been the preferred certification partner for Fortune 500 companies, as well as for medium and smaller businesses.
We serve customers in all industry sectors, but have identified two strategic focus industries: food & beverage and healthcare.
With our extensive local presence, consolidated experience and acknowledged competence in the field of risk management we are an ideal partner for companies in the food production industry.
As the first company in 40 years, DNV was approved by the US government’s center for Medicare and Medicaid (CMS) to accredit (read: certify) hospitals. Working to have an impact on quality and patient safety improvements, DNV developed the NIAHO SM standard against which hospitals are audited and accredited.

## Slide 5: DNVGL: An Independent Foundation
Our Purpose
  To safeguard
  life, property and the environment
Our Vision
  Global impact for a safe and sustainable future
Our Purpose
  To safeguard
  life, property and the environment
Our Vision
  Global impact for a safe and sustainable future
Notes: Our purpose is our reason for being, and has been the same for 140 years, but with the environment now playing a greater role
The vision has two important elements: Firstly, it provides an ambition, namely to have global impact in what we do. This is also why we have seen and will continue to see a strong growth of DNV. It also means that DNV will focus on specific areas.
The other element communicates a direction: We have always worked to improve safety, but the new dimension is to also contribute to sustainable business.

## Slide 6: Accreditation and Beyond

## Slide 7: Key Features
More value, lower $
Focus on sequence and interactions of processes throughout the hospital
ISO 9001 Gradual Introduction @ no additional staff
Demeanor of the survey team
No survey findings “tipping” point
Constant readiness
Collaboration, sharing of ideas
Feature of NIAHO
Benefit to Hospital
Fear becomes confidence
Clear, traceable pathway to improve
Stable standards, infrequent change
Sustainable system
Annual Surveys

## Slide 8: About ISO 9001
Who Developed ISO 9001?
  ISO 9001 was developed through the International Organization for Standardization
    This organization began in 1946 and published the first revision of the ISO 9001 standard in 1987
    The current revision of ISO 9001 is the revision four dated 2015
    The 2015 9001 standard is a Quality Management System that requires the organization to perform risk based thinking
When did ISO 9001 become recognized by healthcare?
  Healthcare has started to embrace ISO 9001 within the last several years, (primarily since 2008)
  More recently with DNV-GL receiving deeming authority from the Centers for Medicare and Medicaid Services, (CMS) to accredit hospitals in 2008, ISO 9001 is rapidly gaining recognition in healthcare

## Slide 9: Integrated Accreditation Model
Integrates ISO 9001 and NIAHO®
  ISO 9001 provides the framework for a sustainable regulatory compliance
  ISO 9001 allows hospitals to use its combined knowledge, wisdom, and innovation to improve quality and safety
  ISO 9001 is the framework within which methodologies such as LEAN and Six Sigma are better understood and utilized
Combined result drives quality transformation into the organization’s core processes
  Performance driven systems produce compliance as a natural outcome

## Slide 10: ISO System Structure
Operational-Business Practices-Regulatory
ISO 9001 Systems

## Slide 11: ISO Management System Standards - Examples
ISO 9001
ISO 27001
Etc.
ISO 50001
ISO 20121 Sustainable Event
ISO 22000
ISO 39001
Road Traffic Safety
ISO 22301 Business Continuity
Etc.
ISO 45001
ISO 20001 IT service mgt.
ISO 14001
Under revision based on new common framework
Already published with
new common framework
All other standards will be revised to the new common framework
Notes: Take a few minutes to have a look at the already published standards available at the class for reference only.
Orange – all other standards on its way!

## Slide 12: Management System Approach
If your organization is currently receiving reimbursement from Medicare/Medicaid, then you are already ~70% compliant with the ISO 9001:2015 Quality Management Standard.

## Slide 13: NIAHO® Surveyors & Survey Activities

## Slide 14: DNVGL Accreditation Progression
1st visit:
  Gain Accreditation to NIAHO® - meet the requirements of CMS
  ISO introduction & education; compliance or certification within 3 years
2nd visit: 1 year after accreditation
  Continue Accreditation by undergoing a survey to NIAHO®
  Survey for progress in implementing ISO 9001
3rd visit: 2 years after accreditation
  Continue Accreditation by undergoing survey to NIAHO®
  Continue to work toward ISO 9001 Implementation (ISO dress rehearsal)
4th visit: 3 years after accreditation
  NIAHO® survey and last year to achieve ISO 9001 compliance/certification
    If in compliance with ISO 9001 – a statement included in Certificate of Accreditation
    May choose to demonstrate compliance by obtaining a separate ISO 9001 Certificate

## Slide 15: DNV Survey Process Innovations
Annual on-site surveys
Collaborative
Less prescriptive
Allows organization innovation
  More than one way to accomplish a goal
  Encourages best practices
  ISO Tenets
    Document what you do
    Do what you document
    Prove it
    Improve it

## Slide 16: Survey Team Composition
Clinical Surveyor
  Patient Care Unit Visits (Clinical Settings)
  Med/ Surg, ICU, CCU, Obstetrics, Emergency Department
  High acuity units
Generalist Surveyor
  Quality Management Review
  Medication Management
  Medical Staff and Human Resources Review
  Utilization Review Interview
  Patient Grievance Interview
  Med/Surg & Ancillary / Support Services Review (Lab, Medical Imaging, Rehab, etc.)
Physical Environment / Life Safety Surveyor
  All Physical Environment aspects and Management Plans
  Physical Environment / Comprehensive Building Tour
  Biomedical Engineering & Calibration of Equipment

## Slide 17: Survey Activities
Survey activities are carried out as follows:
A comprehensive review includes observation of care/services provided to the patient in all patient care areas, patient and/or family interview(s), staff interview(s), and medical record review.
Using Tracer methodology, department/patient unit visits to include staff interviews and open medical record review as appropriate (both clinical and support departments)
    identify performance issues
    handoff between steps
    tracer methodology
Visits to non-clinical support areas
Comprehensive Building Tour (days, not hours)
Notes: 17

## Slide 18: NIAHO® Standard Requirement Chapters
Quality Management System
Governing Body
Chief Executive Officer
Medical Staff
Nursing Services
Staffing Management
Rehabilitation Services
Obstetric Services
Emergency Department
Outpatient Services
Dietary Services
Patient Rights
Infection Control
Medical Records Service
Medication Management
Surgical Services
Anesthesia Services
Laboratory Services
Respiratory Care Services
Medical Imaging
Nuclear Medicine Services
Discharge Planning
Utilization Review
Physical Environment
Organ, Eye and Tissue Procurement

## Slide 19: NIAHO® Physical Environment Management Systems
PE.1 Facility
PE.2 Life Safety Management System
PE.3 Safety Management System
PE.4 Security Management System
PE.5 Hazardous Material (Hazmat) Management System
PE.6 Emergency Management System
PE.7 Medical Equipment Management System
PE.8 Utility Management System
Notes: 19

## Slide 20: NIAHO® and ISO 9001 Quality Management System
Hospital Accreditation: Integration of NIAHO® Standards with ISO 9001 Quality Management System Standards

## Slide 21: Infrastructure and Accreditation
Hospital Patient Care Processes and Supporting Operations
ISO 9001:2015 Quality Management System
(Infrastructure of QMS)
NIAHO℠ Accreditation Requirements
(Consistent with CMS CoPs - Requirement for ISO Compliance/Certification)
CMS (CoPs)
(Accreditation Oversight)
Improved patient care
and safety

## Slide 22: NIAHO® PE.1 Facility

## Slide 23: NIAHO® PE.1 FACILITY
The facility shall be constructed, arranged, and maintained to ensure patient safety, and to provide areas for diagnosis and treatment and for special organization services appropriate to the needs of the community.
SR.1 The condition of the physical plant and the overall hospital environment must be developed and maintained in such a manner that the safety and well-being of patients, visitors, and staff are assured.
SR.2 The hospital must maintain adequate facilities for its services.
  SR.2 a Diagnostic and therapeutic facilities must be located for the safety of patients.
  SR.2 b Facilities, supplies, and equipment must be maintained to ensure an acceptable level of safety and quality.
  SR.2 c The extent and complexity of facilities must be determined by the services offered.

## Slide 24: NIAHO® PE.1 FACILITY ISO 9001-related Requirements
SR.3 The organization shall have policies, procedures and processes in place to manage staff activities, as required and/or recommended by local, State, and national authorities or related professional organizations, to maintain a safe environment for the organization’s patients, staff, and others.
SR.4 The organization shall have a documented process, policies and procedures to define how unfavorable occurrences, incidents, or impairments in the facility’s infrastructure, Life Safety, Safety, Security, Hazardous Material/Waste, Emergency, Medical Equipment, and Utilities Management Systems are prevented, controlled investigated, and reported throughout the organization.
SR.5 The organization shall evaluate the facility’s physical environment management systems at least annually. This evaluation shall be forwarded to Quality Management oversight.
SR.6 Occurrences, incidents, or impairments shall be measured and analyzed to identify any patterns or trends.
SR.8 Significant physical environment data/information shall be disseminated regularly to Quality Management oversight.

## Slide 25: NIAHO® PE.1 FACILITY Common Findings
Failure to have and/or maintain Physical Environment Management Plans
Failure to evaluate Physical Environment Plans
Failure of Leadership to provide support to assure that CAP’s are effective

## Slide 26: NIAHO®PE.2 Life Safety Management System

## Slide 27: NIAHO® PE.2 LIFE SAFETY MANAGEMENT SYSTEM
SR.1 The organization shall meet the applicable provisions of the 2012 edition of the Life Safety Code® of the National Fire Protection Association.
    Note: A hospital must have replaced 1 hour batteries with 1 ½ hour batteries in emergency lighting systems that use batteries as power sources, Chapter 19.2.9, Emergency Lighting.
  SR.2 RESERVED (original standard deleted)
  SR.3 After consideration of the State survey agency findings, CMS may waive specific provisions of the Life Safety Code®, which, if rigidly applied, would result in unreasonable hardship upon the facility, but only if the waiver does not adversely affect the health and safety of patients.
    SR.3a The provisions of the Life Safety Code® do not apply in a State where CMS finds that a fire and safety code imposed by State law adequately protect patients.

## Slide 28: NIAHO® PE.2 LIFE SAFETY MANAGEMENT SYSTEM
SR.4 The organization must have written fire control plans that contain provisions for prompt reporting of fires; extinguishing fires; protection of patients, personnel, and guests; evacuation; and cooperation with firefighting authorities.
  The fire control plan shall provide for the following (NFPA 101-2012, 18.7.2.2 & 19.7.2.2):
        SR.4a. Use of alarms
        SR.4b. Transmission of alarm to fire department
        SR.4c. Response to alarms
        SR.4d. Isolation of fire
        SR.4e. Evacuation of immediate area
        SR.4f. Evacuation of smoke compartment
        SR.4g. Preparation of floors and building for evacuation
        SR.4h. Extinguishment of fire

## Slide 29: Required Barrier Penetration Permit Programs
The Life Safety Management System shall: include in the elements of SR.4d a written plan for the protection of the integrity of hospital smoke and fire barriers.
The plan should include:
  Name(s) of Responsible hospital staff for barrier protection program
  Requirement for written permission for anyone (including all hospital staff, contractors and vendors) to penetrate a smoke or fire barrier wall, ceiling or floor
  Input from Infection Control and Prevention Practitioner on critical clinical areas prior to issuance of written permit for performing work on barriers
  Establishment of monitoring process to ensure all work is completed correctly

## Slide 30: NIAHO® PE.2 LIFE SAFETY MANAGEMENT SYSTEM
SR.5 The organization shall maintain written evidence of regular inspection and approval by State or local fire control agencies.
SR.6 Health care occupancies shall conduct unannounced fire drills, but not less than one (1) drill per shift per calendar quarter that transmits a fire alarm signal and simulates an emergency fire condition. When fire drills are conducted between 9:00 p.m. (2100 hours) and 6:00 a.m. (0600 hours), a coded announcement shall be permitted to be used instead of audible alarms. (NFPA 101-2012, 18.7.1.2. & 19.7.1.2). False alarms may be used (up to 50% of total drills) if all elements of the fire plan are exercised.
  Business occupancies shall conduct at least one unannounced fire drill annually per shift.
SR.6a Fire drills must be thoroughly documented and evaluate the organization’s knowledge to the items listed in PE.2, SR.4
  SR.6 a(1) At least annually, the organization shall evaluate the effectiveness of the fire drills, The report of effectiveness shall be forwarded to Quality Management oversight.

## Slide 31: NIAHO® PE.2 LIFE SAFETY MANAGEMENT SYSTEM
SR.7 The Life Safety Management System shall address applicable Alterative Life Safety Measures (ALSM) that shall be implemented whenever life safety features, systems, or processes are impaired or deficiencies are created or occur. Thorough documentation is required.
  SR.7a. All alternative life safe measures must be approved by the authority having local jurisdiction.
SR.8 The Life Safety Management System shall require that Life Safety systems (e.g., fire suppression, notification, and detection equipment) shall be tested and inspected (including portable systems).
SR.9 The Life Safety Management System shall require a process for reviewing the acquisition of bedding, draperies, furnishings and decorations for fire safety.

## Slide 32: NIAHO® PE.2 LIFE SAFETY MANAGEMENT SYSTEM
SR.10 Construction, Repair, and Improvement operations shall involve the following activities:
  SR.10a During construction, repairs, or improvement operations, or otherwise affecting the space, the Guidelines for Design and Construction of Hospitals and Health Care Facilities, 2010 edition, published by the American Institute of Architects shall be consulted for designing purposes.
  SR.10b The organization shall assess, document, and minimize the impact of construction, repairs, or improvement operations upon occupied area(s). The assessment shall include, but not be limited to, provisions for infection control, utility requirements, noise, vibration, and alternative life safety measures (ALSM).

## Slide 33: NIAHO® PE.2 LIFE SAFETY MANAGEMENT SYSTEM
SR.10c In occupied areas where construction, repairs, or improvement operations occur, all required means of egress and required fire protection features shall be in place and continuously maintained or where alternative life safety measures acceptable to the authority having local jurisdiction are in place.
SR.10d All construction, repairs, or improvement operations, shall be in accordance with applicable NFPA 101-2012 standards, and State and local building and fire codes. Should standards and codes conflict, the most stringent standard or code shall prevail.

## Slide 34: NIAHO® PE.2 LIFE SAFETY MANAGEMENT SYSTEM Common Findings
Failure to evaluate fire drills
ALSM not appropriate or lacking approval from AHJ
Items attached to sprinkler pipe
No Emergency lighting units in areas where deep sedation and general anaesthesia is administered – Condition Level NC
NFPA 99, Health Care Facilities Code, 2012 Edition
6.3.2.2.11 Battery-Powered Lighting Units
6.3.2.2.11.1 One or more battery-powered lighting units shall be provided within locations where deep sedation and general anaesthesia is administered
Failure to correct deficiencies identified on reports
Fire Barrier Program lacking input from Infection Prevention or no evidence of program

## Slide 35: NIAHO®PE.3 Safety Management System

## Slide 36: NIAHO® PE.3 SAFETY MANAGEMENT SYSTEM
SR.1 The organization shall provide a Safety Management System that shall maintain safe and adequate facilities for its services. Diagnostic and therapeutic facilities must be located for the safety of patients.
SR.2 The Safety Management System shall require that facilities, supplies and equipment be maintained and ensure an acceptable level of safety and quality. The extent and complexity of facilities shall be determined by the services offered.
SR.3 The Safety Management System shall require proper ventilation, light and temperature controls in pharmaceutical, food preparation, and other appropriate areas.
SR.4 The Safety Management System shall require that the organization maintain an environment free of hazards and manages staff activities to reduce the risk of occupational related illnesses or injuries.
SR.5 The Safety Management System shall require periodic surveillance of the hospital grounds to observe and correct safety issues that may be identified.
SR.6 The Safety Management System shall address safety recalls and alerts.

## Slide 37: NIAHO® PE.3 SAFETY MANAGEMENT SYSTEM
DNV-GL has adopted Chapter 13 0f NFPA 99 2012
Requires an SVA

## Slide 38: NIAHO® PE.3 SAFETY MANAGEMENT SYSTEM Common Findings
Open junction boxes
Wires not properly terminated
Breaker boxes not properly labelled
Unsafe environments in CEP on roof tops

## Slide 39: NIAHO®PE.4 Security Management System

## Slide 40: NIAHO® PE.4 SECURITY MANAGEMENT SYSTEM
SR.1 The organization shall develop a Security Management System that provides for a secure environment.
SR.2 The Security Management System shall provide for identification of patients, employees and others.
SR.3 The Security Management System shall address issues related to abduction, elopement, visitors, workplace violence, and investigation of property losses.
SR.4 The Security Management System shall establish emergency security procedures to include all hazard events
SR.5 The Security Management System shall require vehicular access to emergency service areas.
SR.6 The Security Management System shall require a process for reporting and investigating security related issues.

## Slide 41: NIAHO® PE.4 SECURITY MANAGEMENT SYSTEM Common Findings
Data not analysed
No clinical restraint training

## Slide 42: NIAHO®PE.5 Hazardous Materials (Hazmat) Management System

## Slide 43: NIAHO® PE.5 HAZARDOUS MATERIAL (HAZMAT) MANAGEMENT SYSTEM
SR.1 The organization shall provide a Hazmat Management System to manage hazardous materials and waste.
SR.2 The HAZMAT Management System shall provide processes to manage the environment, selection, handling, storing, transporting, using, and disposing of hazardous materials and waste.
SR.3 The HAZMAT Management System shall provide processes to manage reporting and investigation of all spills, exposures, and other incidents.
SR.4 The organization monitors staff exposure levels in hazardous environments and report the results of the monitoring to the Quality Management System.

## Slide 44: NIAHO® PE.5 HAZARDOUS MATERIAL (HAZMAT) MANAGEMENT SYSTEM SR.5 Not withstanding any provisions of the 2012 edition of the Life Safety Code to the contrary, a hospital may install alcohol-based hand rub dispensers in its facility if:
  SR.5a. Use of alcohol-based hand rub dispensers does not conflict with any State or local codes that prohibit or otherwise restrict the placement of alcohol-based hand rub dispensers in health care facilities;
  SR.5b The dispensers are installed in a manner that minimizes leaks and spills that could lead to falls;
  SR.5c The dispensers are installed in a manner that adequately protects against inappropriate access
  SR.5d The dispensers are maintained in accordance with dispenser manufacturer guidelines.
  SR.5e If dispensers are stored in corridors, the corridor must be a minimum of 72 inches.
SR.5f The maximum individual dispenser fluid capacity shall be:
      1.2 liters (0.3 gallons) for dispensers in rooms, corridors, and areas open to corridors.
      2.0 liters (0.5 gallons) for dispensers in suites of rooms.
  SR.5g The dispensers shall have a minimum horizontal spacing of 4 ft (1.2m) from each other.
  SR.5h Not more than an aggregate 37.8 liters (10 gallons) of ABHR solution shall be in use in a single smoke compartment outside of a storage cabinet.
  SR.5i Storage of quantities greater than 18.9 liters (5 gallons) in a single smoke compartment shall meet the requirements of NFPA 30, Flammable and Combustible Liquids Code.
  SR.5j The dispensers shall not be installed over or directly adjacent to an ignition source.
  SR.5k In locations with carpeted floor coverings, dispensers installed directly over carpeted surfaces shall be permitted only in sprinklered smoke compartments.
  SR.5l Where minimum corridor width is 72 inches (1830 mm), projections of maximum 6 inches (152 mm) from the corridor wall, above the handrail, shall be permitted for the installation of hand-rub dispensing units.

## Slide 45: NIAHO® PE.5 HAZARDOUS MATERIAL (HAZMAT) MANAGEMENT SYSTEM
SR.6 RESERVED
SR.7 In anesthetizing locations, which use alcohol-based skin preparations, have implemented effective fire risk reductions measures which include:
  SR.7a The use of unit dose skin prep solutions.
  SR.7b Application of skin prep follows manufacture/supplier instructions and warnings.
  SR.7c Sterile towels are used to absorb drips and runs during the application and then removed from the anesthetizing location prior to draping.
  SR.7d Verifying that all of the above has occurred prior to initiating the surgical procedure.
SR.8 Verify that nonflammable medical gas stored outside of an enclosure does not exceed 300 cubic feet per smoke compartment.

## Slide 46: NIAHO® PE.5 HAZARDOUS MATERIAL (HAZMAT) MANAGEMENT SYSTEM
No proper training for handling hazardous and bio hazardous materials
Failure to verify that contractors are competent
Waste not properly stored

## Slide 47: NIAHO® PE.6 Emergency Management System

## Slide 48: NIAHO® PE.6 EMERGENCY MANAGEMENT SYSTEM
SR.1 The organization must provide a comprehensive Emergency Management System to respond to emergencies in the organization or within the community and region that may impact the organization’s ability to provide services.
SR.2 The organization shall meet the requirements set forth in NFPA 99 (2012), Chapter 12, Emergency Management.
SR.3 The Emergency Management System shall require that the organization conduct a hazard vulnerability analysis to identify potential emergencies in the organization and the community.

## Slide 49: NIAHO® PE.6 EMERGENCY MANAGEMENT SYSTEM
SR.4 The Emergency Management System shall establish an emergency process to address the potential hazards to the organization and the community. The hospital shall conduct an organization-wide emergency management exercise, including the triage and disposition of patients. The organization-wide emergency management exercises, including the triage and disposition of patients, shall be conducted no less frequently than twice per year
  SR.4a Emergency management exercises shall test the most threatening hazard(s) identified in the HVA and tax the resources of the organization.
  SR.4b At least every other emergency management exercise shall be conducted with the community to evaluate surge capacity, the integration of Incident Command and intraoperability of communications.
  SR.4c The organization shall formulate an After Action Report of all emergency management exercises to identifying opportunities for improvements and revise its emergency management plan according to the identified opportunities for improvement.

## Slide 50: NIAHO® PE.6 EMERGENCY MANAGEMENT SYSTEM
SR.5 The Emergency Management System processes shall address alternative means to support essential building functions such as electricity, water, ventilation, fuel, medical gas and vacuum systems, and other identified utilities.
SR.6 The Emergency Management System shall include memorandums of understanding for utilization of resources (space, personnel, and equipment) with local and regional healthcare facilities and public health agencies in cases of organizational, community, or regional crisis.
SR.7 The organization shall have policies, procedures, and decision criteria for the determination of protection in place or evacuation of patients in the event of a disaster.

## Slide 51: NIAHO® PE.6 EMERGENCY MANAGEMENT SYSTEM Common Findings
HVA not updated
HVA not effective
No HVA for off-sites or sister properties
Failure to establish CAP for opportunities for Improvement found during drills
Failure to follow up on CAP’s

## Slide 52: NIAHO®PE.7 Medical Equipment Management System

## Slide 53: NIAHO® PE.7 MEDICAL EQUIPMENT MANAGEMENT SYSTEM
SR.1 The organization shall establish a Medical Equipment Management System that provides processes for the acquisition, safe use, and the appropriate selection of equipment.
SR.2 The Medical Equipment Management System shall address issues related to the organization’s initial service inspection, the orientation, and the demonstration of use for rental or physician owned equipment.
SR.3. The Medical Equipment Management System shall address criteria for the selection of equipment.
SR.4 The Medical Equipment Management System shall address incidents related to serious injury or illness or death (See SMDA 1990).

## Slide 54: NIAHO® PE.7 MEDICAL EQUIPMENT MANAGEMENT SYSTEM
SR.5 The Medical Equipment Management System shall have a process for reporting and investigating equipment management problems, failures, and user errors.
SR.6 The Medical Equipment Management System shall address a process for determining timing and complexity of medical equipment maintenance.
SR.7 The Medical Equipment Management System shall address the process of receiving and responding to recalls and alerts.

## Slide 55: CMS S&C 12-07-Hospital Superceded
We are updating previously provided guidance to clarify:
Hospital facilities, supplies and equipment must be maintained to ensure an acceptable level of safety and quality.
A hospital may adjust its maintenance, inspection, and testing frequency and activities for facility and medical equipment from what is recommended by the manufacturer, based on a risk-based assessment by qualified personnel, unless:
  Other Federal or state law; or hospital Conditions of Participation (CoPs) require adherence to manufacturer’s recommendations and/or set specific requirements. For example, all imaging/radiologic equipment must be maintained per manufacturer’s recommendations; or
  The equipment is a medical laser device; or
  New equipment without a sufficient amount of maintenance history has been acquired.
Hospitals electing to adjust facility or medical equipment maintenance must develop policies and procedures and maintain documentation supporting their Alternate Equipment Management (AEM) program. They must adhere strictly to the AEM activities and/or frequencies they establish.

## Slide 56: NIAHO® PE.7 MEDICAL EQUIPMENT MANAGEMENT SYSTEM
No process for “Out of Tolerance “ certificates
Reports not accurate
AEM programs not proper
Failure to analyse data

## Slide 57: NIAHO®PE.8 Utility Management System

## Slide 58: NIAHO® PE.8 UTILITY MANAGEMENT SYSTEM
SR.1 The organization shall require a Utility Management System that provides for a safe and efficient facility that reduces the opportunity for organization-acquired illnesses.
SR.2 The Utility Management System shall provide for a process to evaluate critical operating components.
SR.3 The Utility Management System shall develop maintenance, testing, and inspection processes for critical utilities.
SR.4 The Utility Management System shall contain a process to address medical gas systems and HVAC systems (e.g., includes areas for negative pressure).
SR.5 The Utility Management System shall provide for emergency processes for utility system failures or disruptions.
SR.6 The Utility Management System shall provide for reliable emergency power sources with appropriate maintenance as required

## Slide 59: NIAHO® PE.8 UTILITY MANAGEMENT SYSTEM
SR.7 The Safety Management System shall require proper ventilation, light and temperature controls in operating rooms, sterile supply rooms, special procedures, isolation and protective isolation rooms, pharmaceutical, food preparation, and other appropriate areas.
SR.8 There shall be emergency power and lighting in at least the operating, recovery, intensive care, emergency rooms, and in other areas where invasive procedures are conducted, stairwells, and other areas identified by the organization (e.g., blood bank refrigerator, etc.). In all other areas not serviced by the emergency supply source, battery lamps and flashlights shall be available.
  Emergency lighting standards shall comply with Section 7.9 of Life Safety Code, 101-2000, and applicable references, such as, NFPA-99: Health Care Facilities, for emergency lighting and emergency power.
SR.9 There shall be facilities for emergency gas and water supply.
SR.10 All relevant utility systems shall be maintained, inspected, and tested.

## Slide 60: NIAHO® PE.8 UTILITY MANAGEMENT SYSTEM Common Findings
Numerous findings for generators
No data being reported to leadership

## Slide 61: Number 1 DNV-GL finding in the country
What is the number 1 finding in the country with DNV-GL??

## Slide 62: What is the number 1 finding in the country with DNV-GL?
Failure to analyse data

## Slide 63: What is the number 1 finding in the country with DNV-GL in the Physical Environment?
What is the number 1 finding in the country with DNV-GL in the Physical Environment?

## Slide 64: What is the number 1 finding in the country with DNV-GL in the Physical Environment?
As of January 1, 2017 the number 1 Physical Environment finding in the country with DNV-GL is….
No Emergency lighting units in areas where deep sedation and general anaesthesia is administered NFPA 99, Health Care Facilities Code, 2012 Edition
6.3.2.2.11 Battery-Powered Lighting Units
6.3.2.2.11.1 One or more battery-powered lighting units shall be provided within locations where deep sedation and general anaesthesia is administered
Condition level NC unless resolved while on site!!

## Slide 66: We are judged by the level attained by those whom we serve, and we strive to raise that level as high as possible!
www.dnvaccreditation.com
Kelly Proctor CHFM, CHSP
Kelly.Proctor@dnvgl.com
678-787-9274
DNV GUIDING PRINCIPLE