## Slide 1: Houston Area Association for Hospital Engineering HAAHE
July 13, 2017
Rebecca Read, Architectural Review Group Manager
for Regulatory Services

## Slide 2
DSHS ADOPTS NFPA 99: 2012 Effective Dates
Effective dates:
CMS adopted NFPA 99, 2012 edition: Health Care Facilities Code (HCFC) on May 4, 2016. Federal Register Vol. 81 No. 86
  S&C: 16-29-LSC dated 06/20/2016
  S&C: 16-22-LSC dated 05/06/2016 – Includes HCFC TIA 12-2 through 12-6 and LSC TIA 12-1 through 12-4.
CMS regulation effective date was 07/05/2016.
CMS began surveying for compliance on 11/01/2016.
DSHS informed stakeholders on 10/14/2016 via website under Hot Topics.
DSHS began surveying for compliance on 11/01/2016.
Notes: Please be patience with us and ARG will be learning from you guys so we may be eating crow. If you provide an argument with code references and possibly CMS approval, we will review.
The S&C letter includes the adoption of HCFC TIA 12-2 through 12-6.
The S&C letter includes the adoption of LSC TIA 12-1 through 12-4.

## Slide 3
DSHS ADOPTS NFPA 99: 2012 Effective Dates
CMS adopted NFPA 99, 2012 S&C: 16-29-LSC 06/20/2016
Notes: CMS Survey and Certification memoranda (called S&C memos) are guidance, clarifications and instructions to State Survey Agencies and CMS Regional Offices.
DSHS includes these in there state inspections.
This is included in your packet.

## Slide 4
DSHS ADOPTS NFPA 99: 2012 Effective Dates
DSHS adopts NFPA 99 2012 via hot topics
Notes: This is included in your packet.

## Slide 5
DSHS ADOPTS NFPA 99: 2012 What Facilities are Affected
Surveyed/inspected under NFPA 99, 2012 when all three conditions are met:
Only Hospitals and Ambulatory Surgical Centers (ASC).
The facility will receive Medicare.
The signed and sealed construction drawings and full completed application submittal was received by DSHS ARG on or after July 5, 2016.

## Slide 6
DSHS ADOPTS NFPA 99: 2012 What Facilities are Affected
Facilities under ARG jurisdiction which may be complying with NFPA 99, 2012:
Title 25 Texas Administrative Code Chapter 133 Hospital Licensing State Regulations, Effective June 21, 2007 (last amended September 14, 2014)
Title 25 Texas Administrative Code Chapter 134 Private Psychiatric Hospitals and Crisis Stabilization Units Licensing State Regulations, Effective December 9, 2010 (amended May 24, 2013)
Title 25 Texas Administrative Code Chapter 135 Ambulatory Surgical Centers Licensing Rules, Effective November 25, 2010
Notes: The amended dates applies to licensing. The amendments do not include any physical plant or building systems changes

## Slide 7
DSHS ADOPTS NFPA 99: 2012 What Facilities are Affected
NFPA 99: 2012 overrule the state regulations when NFPA 99: 2012 edition and its referenced publications in Chapter 2 conflict with state rule set.
“Other regulations. The more stringent standard, code or requirement shall apply when a difference in requirements for construction exists.” HLR §133.162 (d)(1)(F) / PPH §134.122 (d)(1)(G) / ASC §135.52 (c)(3)
This code does state the local code, like IBC, must be used if it is more stringent.
Notes: This is when there is a difference from NFPA 2012 99 and NFPA codes under that edition versus state regulations.
If there is a difference in local codes, like IBC, versus the state regulations, the stricter applies. Remember state licensing uses local codes, like IBC, via this code.
Remember these state licensed rule sets are minimum requirements.

## Slide 8
DSHS ADOPTS NFPA 99: 2012 What Facilities are Not Affected
Facilities under ARG jurisdiction which comply with NFPA 99, 2002 edition:
Title 25 Texas Administrative Code Chapter 117 End Stage Renal Disease Facilities Licensing Rules, Effective July 6, 2010
Title 25 Texas Administrative Code Chapter 131 Freestanding Emergency Medical Care Facilities Licensing Rules, Effective June 1, 2010

## Slide 9
NFPA 99: 2012 Planning
Determine type of construction:
NFPA 101, 2012 edition: Life Safety Code, Chapter 43 “Building Rehabilitation”
  This new chapter allows for the application of the requirements for new construction versus the requirements of existing construction to vary based on the type and extent of the rehabilitation work being done. It describes different types of building work, such as repair, renovation, modification, reconstruction, change of use, change of occupancy and addition. Different standards apply to those different situations.

## Slide 10
NFPA 99: 2012 Planning
Be informed:
Facility shall provide a letter on facility letterhead, signed by facility representative, defining anesthetizing locations.
  “Anesthesia. It shall be the responsibility of the governing body of the health care organization to designate anesthetizing. locations”. 1.3.4.2 (2002: 13.2.5) Same in both editions.
This document is required at final inspection.
The language shall be included in narrative as part of ARG submittal package.

## Slide 11
NFPA 99: 2012 Planning
  Facility shall provide a letter on facility letterhead, signed by facility representative, defining wet procedure locations. If not, the operating room is classified as a wet location. 1.3.4.3 /(2002: 13.2.4) same
  Room maybe a shock risk area
Document required at final inspection.
  Definition of wet procedure location. “The area in a patient care room where a procedure is performed that is normally subject to wet conditions while patients are present, including standing fluids on the floor or drenching of the work area, either of which condition is intimate to the patient or staff. 3.3.184 “Operating rooms shall be considered to be a wet procedure locations, unless a risk assessment conducted by the health care governing body determines otherwise”. 6.3.2.2.8.4
    (2002 did not specify operating room as wet or dry location).
  If no letter stating otherwise, ARG inspects for either isolated power or ground-fault interrupters. 6.3.2.2.8.7

## Slide 12
NFPA 99: 2012 Planning
Why be informed?
Wet procedure locations require special protection against electrical shock. 6.3.2.2.8.1
Anesthetizing locations and critical care areas will affect decisions about alarms, zone valves, and WAGD inlets locations.
Piped in medical gases in ASC. Hospitals were always required to have piped in medical gases. ASC state rule set provides an option. If the ASC facility does not receive Medicare, then the ASC is not required to have piped in medical gas. Now if the ASC receives Medicare, it is category 1 or 2 and piped in medical gas is required.
Patient care room definition was enhanced to emphasize the need for area alarms in recovery and emergency rooms.

## Slide 13
NFPA 99: 2012 Planning
What chapters are not applicable?
CMS (therefore DSHS) excluded chapters 7, 8, 12, and 13.
  Federal Register 81 26871 / S&C: 16-29-LSC
Nurse call will be per state rule sets.
  (do not use NFPA 99, 2012 chapter 7).
ARG will not inspect telecommunication equipment room.
  (do not use NFPA 99, 2012 chapter 7).
Notes: Chapter 7 is
Chapter 8 is
Chapter 12 is
Chapter 13 is

## Slide 14
NFPA 99: 2012 Risk Assessment
Conduct risk assessment:
Chapter 4, Fundamentals
  It is now a risk-based code document, compared to a facility-based document in previous editions. Building systems in health care facilities are required to be classified into one of the system categories.
Use documented process to select risk category A4.2
  ISO/IEC 31010: Risk Management-Risk Assessment Techniques.
  NFPA 551: Guide for the Evaluation of Fire Risk Assessments.
  SEMI S10‐0307E: Safety Guideline for Risk Assessment and Risk Evaluation Process.

## Slide 15
NFPA 99: 2012 Risk Assessment
Conduct risk assessment:
Determine the worst-case procedure.
  Determine the level of system category depending on the risks to the caregivers and patients present in the facilities.
  How critical are the systems to patient care/life and caregivers in the facilities?
  Applies to equipment operation, NOT Intervention by caregivers or others.

## Slide 16
NFPA 99: 2012 Risk Assessment
Facility shall provide type of patient care anticipated. Levels of health care services are based on risk to the patients, staff, or visitors in health care facilities.
  “The governing body of the facility or its designee shall establish the following areas in accordance with the type of patient care anticipated and with the following definitions of the classification” 1.3.4.1
  “Patient care room. Any room of a health care facility wherein patients are intended to be examined or treated.” 3.1.138.
  “Patient Bed Location. The location of a patient sleeping bed, or the bed or procedure table of a critical care area.” 3.1.136

## Slide 17
NFPA 99: 2012 Risk Assessment
  Critical care rooms (category 1) – Facility systems in which failure of such equipment or system is likely to cause major injury or death of patients or caregivers. 4.1.1
  General care rooms (category 2) - Facility systems in which failure of such equipment is likely to cause minor injury to patients or caregivers. 4.1.2
  Basic care rooms (category 3) - Facility systems in which the failure of such equipment is not likely to cause injury to patients or caregivers but can cause patient discomfort. 4.1.3
  Support rooms (category 4) - Facility systems in which failure of such equipment would not have impact on patients or caregivers. 4.1.4

## Slide 18
NFPA 99: 2012 Risk Assessment
Category 1: Failure may cause death or serious injury facilities.
  Systems must always work or be available at all times to support patient need (life support).
  Hospital and ASC with full operating room services
  Critical care rooms; such as: angiographic lab, cardiac catheterization labs, coronary care units, hospital inpatient hemodialysis, emergency department, human physiology abs, intensive care units, postoperative recovery, surgical, delivery.
  Category 1 Space means Category 1 piped gases and vacuum. 5.1.1.1
  Category 1 Space means Level 1 EES. NFPA 110: 4.4.1
Notes: In hospital facilities, the dialysis patients are in immediate danger.
Outpatient hemodialysis is not a category 1. Patients are not in immediate danger and can be hand cranked off this device without electricity. But best practice would be to have outpatient ESRD on generator since there are too many patients compared to nurse.
For a go by list of critical care areas, go to appendix A4.1.1

## Slide 19
NFPA 99: 2012 Risk Assessment
Category 2: Failure limited to minor injury.
  High reliability expected of the systems; however, limited short durations of equipment downtime can be tolerated without significant impact on patient care.
  Systems support patient needs but are not critical for life support.
  General care rooms; such as: Med/surg patient rooms, Endoscopy Units, Nursing Homes, Procedural sedation site for outpatient services, cooling towers in Houston.
  Category 2 piped gases and vacuum is very similar to Category 1, with only a few exceptions.
  Category 2 Space means Category 2 piped gases and vacuum.
    This category is intended for applications there treating might require gases occasionally but ordinarily would not. When patients require gases, the need is short. Low intensity surgeries with local anesthesia.
  Category 2 Space means Level 2 EES. NFPA 110: 4.4.2
Notes: It is acceptable to place category 2 on type 2 EES. That is above the requirements so it is acceptable.
HVAC is important to maintain patients from being overheated, so this may be required to be defined as category 2 in hot and humid locations.

## Slide 20
NFPA 99: 2012 Risk Assessment
Category 3: Failure causes discomfort.
  Normal reliability needed of the systems.
  Systems support patient needs but are not critical for life support.
  Basic care rooms; such as: dental office, no general anesthesia rooms, outpatient psychiatric areas, cooling tower in Seattle.
  Not required to have Level 1 or Level 2 EES.
Category 4: No impact on patient’s care or caregivers.
  Loss of system would not be noticeable to patients in the event of failure.
  Typical doctor office’s exam room, morgue, pneumatic tube, waiting room, lounges or lawn sprinkler system.

## Slide 21
NFPA 99: 2012 Electrical
Electrical Receptacles:
4 receptacles minimum powered by both normal power & critical care branch of Level 1 EES 6.3.2.2.1.2 / NFPA 70 517.18. However use the most restrictive NFPA code and NFPA 99 6.3.2.2.6 requires more receptacles.
Allow multi-gang receptacles in patient bed locations.
  “General Care Areas. (B) Patient Bed Location Receptacles. Each patient bed location shall be provided with a minimum of four receptacles. They shall be permitted to be of the single, duplex, or quadruplex type, or any combination of the three...” NFPA 70: 2011 edition: 517.18 (B)
  Critical care areas reads the same but with 6 receptacles. NFPA 70: 517.19 (B)(2)
Notes: Let’s talk about designing now and we will start with electrical. Remember NFPA 99 defines performance requirement for safety. NFPA 70 (NEC) defines installation.

## Slide 22
NFPA 99: 2012 Electrical
Electrical Receptacles:
Must be hospital grade. NFPA 70: 517.18 (B). (same)
Tamper resistant receptacles or listed tamper resistance cover at pediatric 6.3.2.2.6.2 (F)
  (2002: 0) (HLR - 10 patient rooms) (Psych – 10 patients rooms)
  Patient rooms, bathrooms, play rooms, activity rooms.
    “Pediatric Locations. Receptacles located within the rooms, bathrooms, playrooms, activity rooms, and patient care areas of designated pediatric locations shall be listed tamper resistant or shall employ a listed tamper-resistant cover.” NFPA 70: 517.18 (C)
Notes: Let’s talk about designing now and we will start with electrical. Remember NFPA 99 defines performance requirement for safety. NFPA 70 (NEC) defines installation.

## Slide 23
NFPA 99: 2012 Electrical
36 receptacles - Operating Rooms – Cat. 1. 6.3.2.2.6.2 (C)
  (HLR required 16) (ASC required 14)
14 receptacles – Critical Care Areas - Cat. 1. 6.3.2.2.6.2 (B)
  (2002 required 6) (HLR required 12 in special procedure; 14 in NICU, 6 in delivery; 14 in ICU; 8 in ER treatment) (ASC PACU required 6)
8 receptacles – General Care Areas – Cat. 2. 6.3.2.2.6.2 (A)
  (2002 required 4) (HLR required 10 in med/surg, 8 in imaging; 6 in intermediate )(ASC pre-op required 2)
0 receptacles – Bathroom Areas – 6.3.2.2.6.2 (D)
  (2002 required 0) (HLR required 1) (ASC required 0)
0 receptacles – Mental Health/Psych Care Areas – Cat. 1 or 2. 6.3.2.2.6.2 (E)
  (2002 required 0) (HLR required 10) (Psych required 10)
2 receptacles – every 18”-39” OR power strips – Lab – Cat. 2. 6.3.2.3
  (HLR – 1 for refrigerator)
Notes: Categorical Waivers are no longer applicable since NFPA 99 included these waivers in this edition.

## Slide 24
NFPA 99: 2012 Electrical
Power cords allowed if: 10.2.3
  No non-medical devices cannot be connected to cord. 10.5.2.3.6(5)
  Extension chords meet 10.2.4 and 6.3.2.2.6 and 10.5.2.3
  Permanently attached to equipment assembly. 10.2.3.6 (1)
  Sum of ampacity of all appliances connected to outlets not exceed 75 % of ampacity of flexible cord. 10.2.3.6 (2)
No 3-prong to 2 prong adapters 10.2.4
“Locking type receptacles” (used in operating rooms and special procedure rooms) 6.3.2.2.6.1 (B)(2)

## Slide 25
NFPA 99: 2012 Electrical
Electrical Receptacles Testing:
New or replaced:
  Grounding testing for voltage measurements and impedance measurements (10% of all receptacles in patient care vicinity).
  Required document at final inspection: letter state testing meets NFPA 99, 2012 edition: 6.3.3.1.3 and 6.3.3.1.4
    (2002: §4.3.3.1) Same.
  Tested per documented performance manual.
Existing. This applies to each receptacle in patient care rooms (where patient is treated/examined): 6.3.2.2
  Physical integrity.
  Continuity of grounding circuit.
  Polarity.
  Retention force.
Notes: Why only 10% of the receptacles in the patient care room is required to be tested? The intent is to have at least one receptacle tested in each patient care room. It is recommended to test both normal and critical powered receptacles. It is not necessary to test both normal and critical receptacle in one patient room, m=but one normal in one patient room and in the next patient room, test critical receptacle. The 10% random testing should include a mixture of both normal and emergency receptacles.

## Slide 26
NFPA 99: 2012 Electrical
”Grounding System Testing. The effectiveness of the grounding system shall be determined by voltage measurements and impedance measurements.” 6.3.3.1.1 (2002:4.3.3.1.1) same
“The voltage measurements shall be made under no-fault conditions between a reference point and exposed fixed electrical equipment with conductive surfaces in patient care vicinity.” 6.3.3.1.3.1 (2002:4.3.3.1.3) same
“The voltage measurements shall be made with an accuracy of ±20 percent.” 6.3.3.1.3.2 (2002:4.3.3.1.3) same
“Impedance Measurements. The impedance measurement shall be made with accuracy of ±20 percent.” 6.3.3.1.4 (2002:4.3.3.1.4)
“For new construction, the impedance measurement shall be made between the reference point and the grounding contact of 10 percent of all receptacles within the patient care vicinity.” 6.3.3.1.4.1 (2002: 4.3.3.1.4) same
Notes: For existing facilities which have surrendered their license and have applied for an initial license, then receptacle log must be presented. It shall show the physical integrity, continuity of grounding circuit, polarity and retention force. This only applies if no new receptacles have been added. This also applies to renovations; i.e. equipment change out or changing med/surg into a rehab department. Also side note: apply as a minor project. Have the life safety plan ready at the final inspection showing smoke compartments.

## Slide 27
NFPA 99: 2012 Electrical
Line isolation monitor 6.3.2.6.3 / 6.3.2.2.8.4 / 6.3.2.2.8.7
Wet procedure locations require either ground-fault circuit interrupters or isolated power.
Where: Inside room of deep sedation /general anesthesia.
Inspection: (same)
  Green signal lamp visible. 6.3.2.6.3.2 (2002: 4.3.2.6.3.2)
  Red light and alarm for leakage currents. 6.3.2.6.3.2
  Test switch. 6.3.2.6.3.6
Testing, either method is acceptable: 6.3.4.1.4
  Intervals not longer than one month by actuating the LIM test switch.
  LIM with automatic self-test, intervals not longer than 12 months.
    (2002: 4.3.3..3.2.2) same
Notes: Systems (operating rooms considered wet locations, unless risk assessment by governing body (new)

## Slide 28
NFPA 99: 2012 Electrical
Line isolation monitor.
Notes: Systems (operating rooms considered wet locations, unless risk assessment by governing body (new)

## Slide 29
NFPA 99: 2012 Electrical
90 minute battery-powered lighting units: 6.3.2.2.11
Where: Deep Sedation And General Anesthesia Locations.
Why: Backup lighting units are an interim operational mechanism for supplying some measure of lighting in an operating room when power to general lighting is interrupted for any reason.
  Installed in accordance with NFPA 70.
  Connected to the circuits of general lighting in order to monitor them for power. 6.3.2.2.11.3
Life Safety Survey Records
  Test 30 seconds monthly OR 30 minutes annually. 6.3.2.2.11.5

## Slide 30
NFPA 99: 2012 Electrical
  2 independent power sources minimum, 1 must be located on site.
Emergency Power Supply (EPS) Definition:
“The source of electric power of the required capacity and quality for an emergency power supply system. NFPA 110: 3.3.3
  In simple terms, the generator and directly associated components constitute the EPS. ATS are not part of EPS.

## Slide 31
NFPA 99: 2012 Electrical
Emergency Power Supply System (EPSS):
“EPS coupled to a system of conductors, disconnecting means and overcurrent protective devices, transfer switches, and all control, supervisory, and support devices up to and including the load terminals of the transfer equipment needed for the system to operate as a safe and reliable source of electrical power.” NFPA 110: 3.3.4
  In simple terms, ATSs, distribution panels and breakers needed to couple the EPS to the facility, along with the components installed in the facility constitute the EPSS.

## Slide 32
NFPA 99: 2012 Electrical
Types of Levels:
Level 1 is Cat. 1, where failure of equipment could result in loss of life or serious injuries. 4.4.1
Level 2 is Cat. 2, where failure of EPSS is less critical to human life. 4.4.2
Alarms:
Level 1 EPS requires 2 alarms 5.6.6.2
  Local annunciation
  Facility remote annunciator
  Centralized computer system not permitted to substitute alarm annunciator. 6.4.1.1.7.5
Level 2 EPS requires 1 local alarms 5.6.6.2

## Slide 33
NFPA 99: 2012 Electrical
Design:
Separate room. Only EPS and EPSS can be this room. 6.4.1.1.8.1 / NFPA 110 7.2.1.3 / NFPA 110: 7.2.2.3 (same)
Minimize damage from flooding. NFPA 110: 7.2.4 (same)
Accessible to authorized persons only. NFPA 110: 6.5.4
  36 inches around generator. NFPA 110: 7.2.6
    (2002: 30 inches)
Level 1 EPSS not in room where normal service equipment is installed (if over 150 volts/greater 1000 amperes) NFPA 110: 7.2.3 (same)
Final Inspection: submit commissioning report.

## Slide 34
NFPA 99: 2012 Electrical
Design:
Indoor:
  2 hour containment 6.4.1.1.8.1 / NFPA 110: 7.2.1.1 (same)
  40-degree minimum. NFPA 110: 9.3.10.3.6
    (2002: 50 degree minimum in room)
  Heated as necessary to maintain engine water and battery jacket
    Engine water-jacket temperature per manufacturer (2002: 50 degree)
  Exterior air for both ventilation and exhaust (preferably on opposite walls) 9.3.10.3.1 & 9.3.10.3.1.1 / NFPA 110: 7.7.1
    Level 1 requires exterior opening or 2 hour rated air transfer system. 9.3.10.3,2,2, / NFPA7.7.2.2
    No self closing louvers/devices 9.3.10.3.2.3 / NFPA 110: 7.7.2.3
Notes: Internal combustion engine requires both adequate heat to start promptly and adequate ventilation for both avoiding excessive heat and provide air to internal combustion process

## Slide 35
NFPA 99: 2012 Electrical
Design:
Outdoor:
  Resist snow and rain. 7.2.2.1 (same)
  Exterior wall opening OR 2 hour rated air transfer system.
  Ambient air temperature containing Level 1 rotating equipment 40 degrees minimum
    (2002 not stated temperature)
Notes: Internal combustion engine requires both adequate heat to start promptly and adequate ventilation for both avoiding excessive heat and provide air to internal combustion process

## Slide 36
NFPA 99: 2012 Electrical
Generator Lighting:
Level 1 or Level 2 EPS equipment location(s) require battery-powered emergency lighting. This requirement shall not apply to units in outdoor enclosures without walk-in access. 110: 7.3.1 (same)
“The emergency lighting charging system and the normal service room lighting shall be supplied from the load side of the transfer switch.” 110: 7.3.2 (same)
“The minimum average horizontal illumination provided by normal lighting sources in the separate building or room housing the EPS equipment for Level 1 shall be 32.3 lux (3.0 ft-candles) measured at the floor level, unless otherwise specified by a requirement recognized by the authority having jurisdiction.” 110: 7.3.3
  (2002: no horizontal illuminate mentioned).
Notes: Recommended units in housed outdoor units, a flashlight or battery-powered light with a flexible cord be maintained in the housing.

## Slide 37
NFPA 99: 2012 Electrical
Branches for Essential Electrical System: 6.4.2.2
Life safety, critical and equipment branches. Type 1 EES
  (2002: 4.4.2.2.1.1 Life safety and critical called emergency system)
One transfer switch if continuous load of 150 kVa or less. 6.4.2.2.1.4 (B)
  (2002: 4.4.2.2.1.4)
Division of the branches occurs at the transfer switch. 6.4.2.2.1.2

## Slide 38
NFPA 99: 2012 Electrical
Life Safety Branch (Type 1 EES):
Life safety branch 6.4.2.2.3
  (2002: 4.4.2.2.2.2)
Med Gas alarm for Cat. 1 can be on life safety or critical 6.4.2.2.3.3 & Cat. 2 gas alarm on life safety. 6.5.2.2.2.1 (3)(b)
  (2002: 4.4.2.2.2.2. (3)(b) life safety only)
Generator accessories for Cat. 1 on life safety. 6.4.2.2.3.4
  Fuel transfer pumps, receptacles, vent fans, louvers, controls, cooling system and other generator accessories.
  (2002: 4.4.2.2.2.2. (5) did not state the generator accessories. Typically these were located on equipment branch.
  Type 2 EES only task lighting &receptacle. 6.5.2.2.2.1 (6)

## Slide 39
NFPA 99: 2012 Electrical
Life Safety Branch (Type 1 EES):
Fire alarm (same)
  Reminder: Battery in the fire alarm annunciator shall be replaced every five years.
  On battery, label the battery installation date.
Powered doors used for egress for Type 1 EES serving Category 1. 6.4.2.2.3.2 (6) (same)
  Type 2 EES does not include these doors so best practice is to place doors on equipment branch.

## Slide 40
NFPA 99: 2012 Electrical
Life Safety Branch (Type 1 EES):
Type 1 (life safety branch and critical branch) and Type 2 (life safety & equipment): Operable within 10 seconds of losing normal power. 6.4.3.1 / 6.5.3.1
  “The life safety branch shall be so arranged that, in the event of failure of the normal power source, the alternate source of power shall be automatically connected to the load within 10 seconds.” 6.6.3.1.2 and TIA 12-3
Lighting in dining and recreation areas for Cat. 2 (Type 2 EES). 6.5.2.2.2.1 (5)

## Slide 41
NFPA 99: 2012 Electrical
Critical Branch (Type 1 EES):
Cat. 1 (Type 1 EES) has critical branch, Cat. 2 (Type 2 EES) does not have critical branch but life safety and equipment branch only.
Nurse call (same) for Type 1 EES
  Type 2 EES has no mention of nurse call on a certain branch. ARG (having AHJ) will require nurse call on equipment branch.
  Inspection: This is often on life safety and if not on critical branch, this will fail an inspection and facility will be re-inspected. Therefore delay opening the facility.
  On battery, label the battery installation date.

## Slide 42
NFPA 99: 2012 Electrical
Equipment Branch (Type 1 EES). 6.4.2.2.5:
Isolation rooms. Supply, return and exhaust must be operational at final inspection. 6.4.2.2.5 (6)(a)
Nuclear med areas. Supply, return and exhaust must be operational at final inspection. 6.4.2.2.5 (6)(d)
Lab hoods. Point out circuit at final inspection. 6.4.2.2.5 (6)(c)
Elevator recall (DSHS requires one stretcher size) must be operational at final inspection for both Type 1 & 2 EES for floors serving patient areas. 6.4.2.2.5.4 (3)

## Slide 43
NFPA 99: 2012 Electrical
Equipment Branch (Type 1 EES). 6.4.2.2.5:
Surgical, obstetrical delivery, intensive care, nurseries, emergency treatment require supply, return and exhaust. 6.4.2.2.5 (4)
Heating equipment for operating, delivery, labor, recovery, intensive care, nurseries, isolation rooms, emergency treatment and general patient rooms. 6.4.2.2.5 (2)
Autoclave. 6.4.2.2.5 (7)
Best Practice for food service.
  If an on-site food service is provided, power certain appliances on equipment branch.

## Slide 44
NFPA 99: 2012 Medical Gases
Gas and Vacuum Systems - General:
Cat. 1 new or alterations to piping. 5.1.2-5.1.12.3.14.5 & 5.1.14.4.2
Cat. 1 existing piping. Refer to TIA
  Tentative Interim Amendment (TIA) TIA99 12-4 3/27/2013
Central supply system relief valves Cat. 1. 5.1.3.5.6.1.4-9
  (2002: 5.1.3.4.5.1 (3) only final line relief valve vented to outside)

## Slide 45
NFPA 99: 2012 Medical Gases
Central Supply Systems Locations and Positive-Pressure Gases (Liquid Containers) Construction for Cat. 1 & 2:
Containers identified with labels from all directions with 360 degree wraparound tape having 2 inch high letters. 5.1.3.1.3
Lockable door or gate. 5.1.3.3.2 (2)/ 5.2.3.3
  (2002 5.1.3.3.2 (2)) same
Secure cylinders. 5.1.3.3.2 (7)/ 5.2.3.3
  Applies to empty, full, connected, unconnected
  (2002 5.1.3.3.2 (7) state individually secure)
Notes: If there is a code reference with 5.2 then this means category 2 has the same requirements as Category 1. therefore the code reference applies to both category types.

## Slide 46
NFPA 99: 2012 Medical Gases
Labeling slightly different. Use “Positive Pressure Gases”. Doorway labeling of locations containing central supply systems and cylinder storage. 5.1.3.1.8/ 5.1.3.1.9 / 5.2.3.1
  (2002: 5.1.3.1.5 / 5.1.3.1.6 stated the word “Medical Gases”)
Cylinders can not share room with central supply system if central supply system room contains motor-driven machinery. 5.1.3.3.4 / 5.2.3.3
  No storage requirements for 300 cubic feet and less of non-flammable compressed gas per smoke compartment.
    CMS S&C-07-10
Notes: If there is a code reference with 5.2 then this means category 2 has the same requirements as Category 1. therefore the code reference applies to both category types.

## Slide 47
NFPA 99: 2012 Medical Gases
    Protect electrical devices per 70: 5.1.3.3.2 (5) and protected from physical damage. 5.1.3.3.2 (10)
  (2002: 5.1.3.3.2 (5) stated 5’ AFF)
Indirect heat, if applicable. 5.1.3.3.2 (6) same
Access to move cylinders on hand trucks. 5.1.3.3.2 (1)
  (2002: 5.1.3.3.2 (1) no mention of hand trucks).
  Do not use room as storage (often a deficiency).
  Do not be stored in a tightly closed space. Therefore do not cram them in a tiny room (often cited in life safety surveys in ASC).
Notes: If there is a code reference with 5.2 then this means category 2 has the same requirements as Category 1. therefore the code reference applies to both category types.

## Slide 48
NFPA 99: 2012 Medical Gases
Indoor enclosure: 5.1.3.3.2. (4)
  1-hour rated (often a deficiency in ASC) (same)
  Interior finishes that are noncombustible or include limited combustible materials. (same)
  Cylinders should always be kept in ventilated spaces so gas that leaks can disperse safely. 5.1.3.3.1/5.1.3.5.6.1 (4-9)
    (2002: 5.1.3.3.3.1)
  Natural ventilation - “Mechanical ventilation shall be provided if natural ventilation requirements can not be met.” 9.3.7.5.2.5
    (2002: code does not prioritize natural ventilation.)
    Nonclosable louvered opening 1 foot of floor & 1 foot of the ceiling. 9.3.7.5.2.1 / 9.3.7.5.2.2
    Openings ensure cross ventilation. 9.3.7.5.2.3
    No ductwork for natural ventilation. 9.3.7.5.2.4
    Nonclosable louvered opening each 24 sq. in./1000 cu.ft. 9.3.7.5.2.1
Notes: If there is a code reference with 5.2 then this means category 2 has the same requirements as Category 1. therefore the code reference applies to both category types.

## Slide 49
NFPA 99: 2012 Medical Gases
Indoor enclosure (continued):
  Mechanical ventilation 9.3.7.5.3
    2002: greater than 3,000 cu, ft. enclosed vented to outside.
    Mechanical exhaust fans shall provide not less than 50 cfm or more than 500 cfm. Size is based on gas contained in the largest single vessel in the room or in one header bar of cylinders. 9.3.7.5.3.2
    Draw air 1 foot of floor and unobstructed (facilities usually obstruct duct). 9.3.7.5.3.3
    Maintain negative pressure continuously. 9.3.7.5.3.1
    125-degree maximum temperature. 9.3.7.6
    Exhaust powered from EES. 9.3.7.5.3.4
      Final inspection will verify that circuit.

## Slide 50
NFPA 99: 2012 Medical Gases
Indoor enclosure (continued):
  Life safety surveys: Cited often the obstruction air duct which is drawing air 1 foot of the floor. Best Practice is to tape off that location so nothing blocks the air draw.
  Inspection: Be prepared to show the circuit for the mechanical exhaust.

## Slide 51
NFPA 99: 2012 Medical Gases
Outdoor enclosure:
  Enclosed by noncombustible fence or wall. 5.1.3.3.2 (3)/ 5.2.3.3
    (2002 5.1.3.3.2 (3)) same
  2 entry/exits minimum 5.1.3.3.2 (3)/ 5.2.3.3 (new)
  When imperable walls, openings at base of each wall for free air circulation. 5.1.3.3.3.3 (A)/ 5.2.3.3 (same)
    Impermeable enclosures shared with other enclosures no ventilation openings at base of enclosure. 5.1.3.3.3.3 (B)/ 5.2.3.3 (new)
Notes: If there is a code reference with 5.2 then this means category 2 has the same requirements as Category 1. therefore the code reference applies to both category types.

## Slide 52
NFPA 99: 2012 Medical Gases
Outdoors:
  “If located outdoors, be installed in an enclosure used only for this purpose and sited to comply with minimum distance requirements in NFPA 55.” 5.1.3.5.10 (1)
    Was NFPA 5.1.3.4.10.1
  Central supply systems for nitrous oxide and carbon dioxide/ cylinder temperature is 125 degree maximum. 9.3.7.7
    These two gases exist as a liquid in the cylinder at room temperature and the vaporization rate significantly diminishes at lower temperatures, which can cause the supply systems to malfunction or possibly fail.
      (2002: 5.1.3.3.1.7 was 130 degrees).

## Slide 53
NFPA 99: 2012 Medical Gases
Adopters:
The use of adapters or conversion fittings to adapt from one gas-specific fitting to another is NOT allowed. 5.1.3.2
  This is meant to eliminate the chance of cross-connections causing the wrong gas to be administered to a patient, which is one of the major causes of accidental deaths with medical gas systems.

## Slide 54
NFPA 99: 2012 Medical Gases
Medical Air Compressor Intake:
Requirements:
  Draw air from a source of clean air. 5.1.3.6.3.12 (A) same
  Located 25 feet minimum from ventilating system exhausts, fuel storage vents, combustion vents, plumbing vents, vacuum & WAGD discharges, or areas that can collect vehicular exhausts or noxious fumes. 5.1.3.6.3.12 (B) new
    (2002: 5.1.3.5.13..2 above roof level only)
  Located 20 feet minimum above ground. 5.1.3.6.3.12 (C)
  Located 10 feet minimum from any door, window, or other opening in the building. 5.1.3.6.312 (D) same
    (2002: 5.1.3.5.13.2)

## Slide 55
NFPA 99: 2012 Medical Gases
Medical Air Compressor Intake Requirements (Continued):
  Used filters air from hospital if air supply continuous for 24 hours and motors/drive belts are not located in the airstream of medical air intake 5.1.3.6.3.12 (E) same
  Piping of the system meets 5.1.10.2 same
  Air intakes for separate compressors combined into one if: 5.1.3.6.3.12 (G) same
    Common intake is sized to minimize backpressure
    Each compressor can be isolated to eliminate backpressure if compressor is removed from service.
  Air End of intake turned down & screened. 5.1.3.6.3.12 (H) new

## Slide 56
NFPA 99: 2012 Medical Gases
Instrument Air:
Examples: all operated booms, surgical tools, remove excess moisture from instruments or used in labs 5.1.3.9.2.1
  Indoors in dedicated mechanical equipment vented area. 5.1.3.9.2.2 9 (1) same
Prohibited from: 5.1.3.9.2.3
  Interconnection with medical air systems.
  Usage for any purpose where the air will be intentionally respired by patients or staff.
    (2002: 5.1.3.8.2.3) (HLR table 6 note 3) same

## Slide 57
NFPA 99: 2012 Medical Gases
Medical Gases– Cat. 1:
General:
  Piped medical gases separated from instrument air. 5.1.3.5.2
  Medical gases are not to be used for things like blowing out or drying scopes. Support Gases (Nitrogen or Instrument Air) can be used to provide power for surgeons tools, brakes for orbital arms in surgery, and drying medical equipment. They cannot be used for breathing purposes
  “Uses of Medical Air Medical air sources shall be connected to the medical air distribution system only and shall be used only for air in the application of human respiration and calibration of medical devices for respiratory application.” 5.1.3.6.2

## Slide 58
NFPA 99: 2012 Medical Gases
Vacuum Pump Exhaust for Cat. 1:
Requirements:
  Exhausted to outdoors. 5.1.3.6.7.2 (1) (same)
  10 feet away from opening. (same)
  Turned down and screened. 5.1.3.7.7.3 (same)
Exhaust is the same as medical-surgical vacuum source exhaust. 5.1.3.7.7 / 5.1.3.8.6 (same)
Removal of excess anesthetic gases from anesthesia circuit by Waste Anesthetic Gas Disposal (WAGD). 9.3.8.1
WAGD inlet located in all locations where nitrous oxide or halogenated anesthetic gas is intended to be administered.

## Slide 59
NFPA 99: 2012 Medical Gases
Medical Gas Zone Valve for Cat. 1:
Wall intervenes between zone valve and outlet that zone valve. controls. Use line of sight. (often cited) 5.1.4.8 (2002:5.1.4.8) same
Zone valve not in same room with outlets that zone valve controls. 5.1.4.8.(3)
  (2002 not stated)
Zone valves readily operable from standing position. 5.1.4.8.1 same
Zone valve visible and accessible at all times. 5.1.4.8.4 same (often cited)
Zone valve not behind doors (open doors/closed doors). 5.1.4.8.5 same
Not located in closed rooms; i.e: not in janitor closet. (often cited ASC)
Immediately outside life support area, critical care area and anesthetizing location (OR). 5.1.4.8.7 same
Notes: If use deep sedation, moderate anesthesia or general anesthesia, then zone valve outside that room. IE: MRI at children hospital.
Deep sedation and General anesthesia: patients cannot be easily aroused. Moderate anesthesia patients respond to verbal commands

## Slide 60
NFPA 99: 2012 Medical Gases
Alarms for Cat. 1:
2 master alarms: 1) in office of on-site individual responsible for maintenance and 2) constantly observed location, IE: switchboard, ER nursing station. 5.1.9.4.1 (computer is new)
One of the two can be substituted with centralized computer system.
  (2002 not allow this substitution)
Labeling of alarms where room numbers is accurate. 5.1.9.1 (13)
Joining commons is not allowed in alarm wiring.
Master alarm wiring splices are allowed at junction boxes.
Switches / sensors installed so as to be removable. 5.1.9.1 (14) (new)
Area alarm panels shall provide visual & audible indication in the event a mismatch occurs between transducer(s) and its associated circuit board(s).” 5.1.9.3 (new).

## Slide 61
NFPA 99: 2012 Medical Gases
Differences from Cat.1 and Cat. 2:
Cat. 1 means patients require gases and Cat. 2 is intended for applications to facilities treating patient who might require the gases occasionally by ordinarily would not. Those who need gases is short term. Lives at minimal risk if gases fail and gases rarely used.
Cat. 2 meet Cat. 1 requirements except some equipment permitted to be simplex. (Cat. 1 is required to be duplex).

## Slide 62
NFPA 99: 2012 Medical Gases
Differences from Cat.1 and Cat. 2:
Cat. 2 simplex. 5.2.3.5 / 5.2.3.6 / 5.2.3.7
  Medical air compressors, dryers, aftercoolers, filters and regulator.
  Medical-Surgical vacuum.
  WAGD.
Cat. 2 alarms. 5.2.9
  Single alarm panel for warning systems.
  Located in area of continuous surveillance (IE: recovery nurse station).
  Pressure and vacuum switches mounted at source. equipment with pressure indictor at master alarm panel.
  Maintenance. 5.2.14

## Slide 63
NFPA 99: 2012 Medical Gases
Maintenance/Testing for Cat. 1:
Life safety surveys records: annual testing of the med gas system is to be conducted by ASSE 6040 credentialed Medical Gas Maintenance Personnel. 5.1.14.2.1 / 5.1.15
  Document periodic maintenance programs for their medical gas systems.
  Inventories shall include sources, control valves, alarms, manufactured assemblies and outlets.
Inspections:
  Provide verifier credential (photocopy of ASSE 6030).
  Provide Journeyman credential.
  If modification (breach), test downstream portion . 5.1.14.4.1/5.1.14.4.6

## Slide 64
NFPA 99: 2012 Medical Gases
Gas Systems Installer. This certification applies to anyone installing medical gas and vacuum systems. It includes anyone who works on or installs equipment, piping, components or conducts any brazing procedures.
  Identification required at final inspection.
ASSE 6020 Medical Gas Systems Inspector. This certification applies to anyone who inspects the installation of medical gas and vacuum systems.
ASSE 6030 Medical Gas Systems Verifier. This certification applies to anyone who tests, verifies or certifies the installation of medical gas and vacuum systems.
  Identification required at final inspection.
ASSE 6040 Medical Gas Systems Maintenance Personnel. This certification applies to anyone who maintains medical gas and vacuum systems.
  Certifications typically are through in-class instruction.

## Slide 65
NFPA 99: 2012 Sprinkler System
Extinguishing systems:
If work exceeds 50% of floor area of story, entire story sprinkler system must be brought up to requirements of new occupancy. NFPA 101: 43.6.4.1.
If work exceeds 50% throughout the building, entire building sprinkler system must be brought up to requirements of new occupancy from top floor containing rehabilitation and all below floors.
4 hours or more of fire alarm system being out of service, then fire watch or evacuate. NFPA 101: 9.6.1.6
10 hours of a fire sprinkler being out of service, then fire watch or evacuate. 18.2.2.2.5.2 / FR 20.3.5

## Slide 66
NFPA 99: 2012 Sprinkler System
Extinguishing systems (continued):
Sprinklers not required in patient sleeping room closet if both conditions are met: 15.8.1.3
  Closet not exceed 6 square feet
  Distance does not exceed max. distance per NFPA 13. NFPA 101: 18.3.5.10
Fire Alarm Zones :
Fire alarm zones shall be permitted to alarm for individual smoke compartments. This does not apply to sprinkler systems. Zoned water flow is prohibited. NFPA 101: 18.3.4.3.3.3

## Slide 67
NFPA 99: 2012 HVAC
Smoke Evacuation:
No longer required. CMS did not adopt this requirement in its final rule.
  The requirement for non-recirculation of smoke and venting products of combustion from an anesthetizing location contained in the 2005 edition under environmental systems (Chapter 6) has been removed.
  Federal Register section 18.3.2.3 and 20.3.2.3 has this in it. However per documentation from CMS representative, smoke evac in windowless rooms having deep sedation and general anesthesia locations is not required.
  Use of flammable anesthetics was common and many were unsprinklered. Therefore the fire hazards in these rooms was much higher.
Notes: Pushback occurred when CMS wanted to exempt this rule and maintain the smoke evac system. Pushback was system poses infection control risks and unreliable.

## Slide 68
NFPA 99: 2012 HVAC
Smoke Evac at Anesthetizing Locations applications:
  Existing occupancy with smoke control installed: Maintain to edition of code at installation OR completely remove smoke exhaust fans only after the facility is in full compliance with 2012 NFPA 99
  Existing occupancy without smoke control installed: No smoke control system required if the facility is in full compliance with 2012 NFPA 99
  New occupancy: No smoke control system required if the facility is in full compliance with 2012 NFPA 99

## Slide 69
NFPA 99: 2012 Kitchen
Cooking Facilities: Federal Register 18.3.2.5.3
Allowed in a smoke compartment where food is prepared and permitted to be open to the corridor if all are met:
  30 individuals or fewer (by bed count).
  Separated from other portions of the facility by a smoke barrier.
  2 smoke detectors located no closer than 20 feet and not further than 25 feet from the cooktop or range.
  Range hood and stovetop have 1) switch must be located in the area that is used to deactivate the cook top or range whenever the kitchen is not under staff supervision. 2) Switch also has a timer, not exceeding 120-minute capacity that automatically shuts off after time runs out.

## Slide 70
NFPA 99: 2012 Heaters
Suspended Heaters: (new)
Allowed, but not in means of egress or patient sleeping areas. NFPA 101: 18.5.2.3(1)/18.5.2.2.(2)
  High enough to be out of reach of persons
  Safety feature that stops fuel flow and shuts down heater when excessive temperature or ignition failure occurs.

## Slide 71
NFPA 99: 2012 Fireplaces
Fireplaces:
Federal Register section Sections 18.5.2.3 and 19.5.2.3 — Fireplaces
Direct-vent gas fireplaces allowed in smoke compartments where patient sleep (but not patient sleeping room: NFPA 101: 18.2.5.3/9.2.2
  No rated walls
  Sealed glass front and wire mesh screen
  Combustion air connections between appliance and vent-air intake terminal and combustion air from outside
  Flue-gas connections between the appliance and the vent-air intake terminal and all flue gases are discharged to outdoor atmosphere
  Sprinklered compartment (quick response)
  Control for fireplace in locked/restricted location
  Electronically supervised carbon monoxide detector
    2002 required 1-hour walls.

## Slide 72
NFPA 99: 2012 Fireplaces
Fireplaces:
Solid fuel-burning fireplaces allowed in smoke compartments where no patients sleep: 101:18.5.2.3(3)
  1-hour rated wall separating patient sleeping spaces
  4” minimum high hearth
  Electronically supervised carbon monoxide detector in same room and connected to building fire alarm panel
  Enclosure rated up to 650 degree temperature with heat tempered glass.

## Slide 73
NFPA 99: 2012 Design Summary
Summarize:
Fire Safety Final Rule outlines the requirements for certain Medicare and Medicaid certified providers and suppliers to meet certain fire safety requirements. The final rule includes the adoption of the 2012 edition of the LSC, NFPA 101 and additionally the adoption of the 2012 edition of the Health Care Facilities Code, NFPA 99. The regulation does away with the use of the 2000 edition of the LSC and associated reference documents.
DSHS adopted HCFC 99 for certain facilities.

## Slide 74
DSHS INSPECTIONS Deficiencies
Deficiencies at Final Inspection
  Exam lights missing. (no 2x4 lights).
  Bonding. NFPA 70: 517.14 (same)
  Exit signs at won door in shut position & at fur down not see.
  Label electrical receptacles and med gas according to placard.
  Permanent labels on boom’s electrical receptacles. 6.4.2.2.6.2 (C)
  Space in front of electrical panel boards.
  Normal and emergency power in the same room without double clearance.
  ASC elevator must be on generator.

## Slide 75
DSHS INSPECTIONS Deficiencies
Deficiencies at Final Inspection
  Nurse call shall be on critical branch of Type 1 EES. Many times it is not.
  Nurse call and fire alarm on battery backup if temporary generator.
  Duty station missing in equipment storage.
  Fire alarm annunciator panel shall be visual in nurse station.
  Audible fire alarms too loud.
  Sinks missing at any patient treatment/care areas. This includes speech therapy, lab etc.

## Slide 76
DSHS INSPECTIONS Deficiencies
Deficiencies at Final Inspection
  Kill switch shall be provided at all AHU.
  Pressurization.
  Filters shall be clean and installed.
  Ventilation in med gas room.
  Only rated rooms are med gas and normal electrical room in ASC, ESRD, FEC.
  Smoke evac fully operational (outside and inside air, detector in anesthesia rooms) for facilities under NFPA 99: 2002.
  Cannot share systems between different facilities.

## Slide 77
DSHS INSPECTIONS Deficiencies
Deficiencies at Final Inspection
  Monument sign must be installed.
  No flex for receptacles powered by generator. 6.4.2.2.6.4
  Yes cath lab and IR radiology is invasive and must have a ASC license.
  All ASC must be licensed. For outpatient department of hospital, not in hospital footprint, must be licensed AC.
  Ambulatory service facilities can exit through another area but all egress powered by generator.
  Door locking arrangements. 18.2.2.2.5.2 & TIA 12-4
  If critical wiring is in same junction box as normal, separate by metal (not plastic) divider. ARG will have cover plates removed if red light switch is in same faceplate as white light switch. 6.4.2.2.6.1
Notes: Interior doors to be locked, subject to the following requirements: (1) All staff must have keys; (2) smoke detection systems must be in place; (3) the facility must be fully sprinklered; (4) the locks are electrical locks that will release upon loss of power to the device; and (5) the locks release by independent activation of the smoke detection system and the water flow in the automatic sprinkler system.

## Slide 78
DSHS INSPECTIONS ASC
Definition of ASC
The definition of an ASC is as follows: A facility that primarily provides surgical services to patients who do not require overnight hospitalization or extensive recovery, convalescent time or observation.
Although the Texas Ambulatory Surgical Center Licensing Act does not define surgical services, the Medical Practice Act defines surgery to include “surgical services, procedures, and operations” as well as “the procedures described in the surgery section of the common procedure coding system as adopted by” what is now known as the Centers for Medicare and Medicaid Services (CMS).
CMS in its interpretive guidelines for 42 CFR §482.51 Surgical Services defines surgery to include incision; treatment with any instruments causing localized alteration or transposition of live human tissue; and injection of diagnostic or therapeutic substances.
CMS in Pub 100-03 Medicare National Coverage Determinations defines surgery as “operative procedures in which skin or mucous membranes and connective tissue are incised or an instrument is introduced through a natural body orifice. Invasive procedures include a range of procedures from minimally invasive dermatological procedures (biopsy, excision, and deep cryotherapy for malignant lesions) to extensive multi-organ transplantation. They include all procedures described by the codes in the surgery section of the Current Procedural Terminology (CPT) and other invasive procedures such as percutaneous transluminal angioplasty and cardiac catheterization. …”
Notes: If patient rendered incapable of self-preservation, uses general anesthesia, or provides emergency services that one would expect to receive patients that due to the nature of their injury are incapable of self-preservation

## Slide 79
DSHS INSPECTIONS ASC
Definition of ASC (continued)
In addition, The 2002 edition of the National Fire Protection Association’s NFPA 99, Health Care Facilities Code section 3.3.87 defines an invasive procedure as “Any procedure that penetrates the protective surfaces of a patient’s body (i.e. skin, mucous membrane, cornea) and that is performed with an aseptic filed (procedural site).”
NFPA 99 2012 section 4.1.1 defines Category 1 as facility systems in which failure of such equipment or system is likely to cause major injury or death of patients or caregivers shall be designed to meet system Category 1 requirements as defined in this code.
Therefore, if a specific procedure meets the definitions as stated above, the procedure must be performed in a licensed ASC or Hospital.

## Slide 80
DSHS CONTACTS Regulatory
Commissioner of Health– John Hellerstedt, MD
  512-776-7363
Associate Commissioner for Regulatory Services: Jon Huss
  512-834-6660
Regulatory Licensing Unit Manager: Charlotte Sullivan Ed. D
  512-834-6600 ext. 6703
Facility Licensing Group (FLG)– Pamela Adams
  512-834-6600 ext. 2607
Architectural Review Group Manager – Rebecca Read
  512-834-6649

## Slide 81
DSHS CONTACTS Architectural Review Group
Architectural Review Group (ARG) 512-834-6649
first name.last name@ dshs.texas.gov
https://www.dshs.texas.gov/facilities/architectural-review.aspx
  Administration: 4 staff handle 1,000 calls & 400 letters monthly
    Ginger Smith – Administration team lead
    Kerry Terry – Distributor - status of project
    Nkpola Ukandu - Scheduler
    Robert Martin* – Intake processor - status of submittal or faxes
  Inspectors: 7 staff handle 85 inspections & 40 feasibility monthly
    Angel Alvarez Glenn Crow JB White* Mark Antilley * Pei Basgen* Robert Floan Sinh Nguyen
Notes: This email address applies to everyone at DSHS. This email address will change on September 1, 2017
Pei-Hua.Basgen Jon.antilley John.white RobertA.martin

## Slide 82
DSHS CONTACTS Architectural Review Group
Physical address: (for feasibility conferences and over-night packages- Federal Express, UPS, DHL, LSO):
  Texas Department of State Health Services Architectural Review Group (MC 2835) 8407 Wall Street Austin, TX 78754
Mail (United States Postal Service):
  Texas Department of State Health Services PO Box 149347 Architectural Review Group (MC 2835) Austin, TX 78714-9347
Notes: This both addresses will change on September 1, 2017.
ARG forms will therefore change on September 1, 2017. therefore call for new forms. Hopefully they will be changed on website but no effective date committed as of yet.. So throw away all ARG forms September 1, 2017 that your office has.

## Slide 83
DSHS CONTACTS Facility Licensing Group
Licensing:
  Angela Arthur 512-834-6648 ext. 2633
    Hospitals – both General and Special
      2001: 519 facilities 2017.07: 652 facilities
    Special Care Facilities (SCF)
      2001: 6 facilities 2017.07: 12 facilities
    Private Psychiatric Hospitals
      2001: 28 facilities 2017.07: 57 facilities
    Crisis Stabilization Units (CSU)
      2001 – 2015 3 facilities 2017.07: 5 facilities
    Free Standing Medical Care Facilities (FEMC)
      2010: 19 facilities 2017.07: 220 facilities
Notes: If you use extension, then the phone number is 512-834-6600

## Slide 84
DSHS CONTACTS Facility Licensing Group
Licensing:
  Crystal Govan 512-834-6648 ext. 2617
    Ambulatory Surgical Centers
      2001: 217 facilities 2017.07: 481 facilities
  Krystal Cantu 512-834-6648 ext. 2605
    Birthing Facilities
    End Stage Renal Disease Facilities
      2001: 283 facilities 2017.07: 688 facilities
  Pamela Adams 512-834-6600 ext. 2607
    Abortion Facilities
  Genesis Villanueva 512-834-6648 ext. 2016
    Substance Abuse Facilities (residential substance abuse)
    Narcotic Treatment Program (NTP) Faith Based

## Slide 85
DSHS CONTACTS General
Complaints
    Mail: Patrice Kennemer, Customer Service Coordinator
    PO Box 149347, MC-1913, Austin, Texas 78714-9347 Phone: (512) 776-2150 or 1-888-963-7111, ext. 2150 E-mail: customer.service@dshs.texas.gov
Open Records
  HealthFacilitiesOpenRecords@dshs.texas.gov
Waiver: (mail hard copy waiver & email waiver)
  Lisa Peers 512-834-6648
    DSHS, Regulatory Licensing Unit
    Facility Licensing Group Nurse Consultant
    P.O. Box 149347, Mail Code 2835
    Austin, Texas 78714

## Slide 86
DSHS CONTACTS Health Compliance
Health Facility Compliance
Branch Manager – Patrick Waldron, M.Ed., LMSW
  512-834-6700 ext. 2625
Central Manager Zone I: Wanda Wilson 512-834-6700 x. 2685
Arlington Manager Zone II: Shannon Sisco 817-264-4500
San Antonio Manager Zone III: Larrie Collier 210-531-7319
Houston Manager Zone 4: Frank Arch 713-767-3360
Tyler Manager Zone 5:Jeannette Potter 903-533-5381
State Wide Manager 6: Rachel Turner 512-834-6700 x 2639
CLIA: Sue Zimmerman 512-834-6700 ext. 2603

## Slide 87
DSHS CONTACTS Other
Hot Topics:
  https://www.dshs.texas.gov/facilities/news.aspx
    Why is this important:
      September 1, 2017 ARG moves to HHS from DSHS
      ARG will have a different mailing information
Federal Register:
  https://www.federalregister.gov/
  Search “81 FR 26871” dated 5/4/2016
CMS S&C letters:
  https://www.cms.gov/Medicare/Provider-Enrollment-and-Certification/SurveyCertificationGenInfo/Policy-and-Memos-to-States-and-Regions.html
Notes: CMS Survey and Certification memoranda, guidance, clarifications and instructions to State Survey Agencies and CMS Regional Offices.

## Slide 88: THANK YOU
Rebecca Read, Architectural Review Group Manager
for Regulatory Services